## Index
Model | Label | Description | Detailed Description
701 | DER AC Measurement | DER AC measurement model.
702 | DER Capacity | DER capacity model.
703 | Enter Service | Enter service.
704 | DER AC Controls | DER AC controls model.
705 | DER Volt-Var | DER Volt-Var model.

## 701
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description
|  | DERMeasureAC |  |  | group | [6 empty] | DER AC Measurement | DER AC measurement model.
0 |  | ID | 701 |  | uint16 |  |  |  |  | M | S | DER AC Measure Model ID | DER AC measurement model id.
1 |  | L |  |  | uint16 |  |  |  |  | M | S | DER AC Measure Model Length | DER AC measurement model length.
Wiring Type
2 |  | ACType |  |  | enum16 | [6 empty] | AC Wiring Type | AC wiring type.
|  | SINGLE_PHASE | 1 | [8 empty] | Single phase
|  | SPLIT_PHASE | 2 | [8 empty] | Split phase
|  | THREE_PHASE | 3 | [8 empty] | Three phase
Operating State
3 |  | St |  |  | enum16 | [6 empty] | Operating State | Operating state of the DER.
|  | OFF | 1 | [8 empty] | Off
|  | ON | 2 | [8 empty] | On
|  | WARNING | 3 | [8 empty] | Warning | There is an active alarm, device is able to generate with possible constraints.
|  | ERROR | 4 | [8 empty] | Error | There is an active alarm, device is not able to generate due to one or more of the alarm issues.
Grid Connection State
4 |  | ConnSt |  |  | enum16 | [6 empty] | Grid Connection State | Grid connection state of the DER.
|  | DISCONNECTED | 1 | [8 empty] | Disconnected | Disconnected from the grid.
|  | CONNECTED | 2 | [8 empty] | Connected | Connected to the grid.
Alarms
5 |  | Alrm |  |  | bitfield32 | [6 empty] | Alarm Bitfield | Active alarms for the DER.
|  | GROUND_FAULT | 0 | [8 empty] | Ground fault
|  | DC_OVER_VOLT | 1 | [8 empty] | DC over voltage
|  | AC_DISCONNECT | 2 | [8 empty] | AC disconnect open
|  | DC_DISCONNECT | 3 | [8 empty] | DC disconnect open
|  | GRID_DISCONNECT | 4 | [8 empty] | Grid disconnect
|  | CABINET_OPEN | 5 | [8 empty] | Cabinet open
|  | MANUAL_SHUTDOWN | 6 | [8 empty] | Manual shutdown
|  | OVER_TEMP | 7 | [8 empty] | Over temperature
|  | OVER_FREQUENCY | 8 | [8 empty] | Frequency above limit
|  | UNDER_FREQUENCY | 9 | [8 empty] | Frequency under limit
|  | AC_OVER_VOLT | 10 | [8 empty] | AC Voltage above limit
|  | AC_UNDER_VOLT | 11 | [8 empty] | AC Voltage under limit
|  | BLOWN_STRING_FUSE | 12 | [8 empty] | Blown String fuse on input
|  | UNDER_TEMP | 13 | [8 empty] | Under temperature
|  | MEMORY_LOSS | 14 | [8 empty] | Generic Memory or Communication error (internal)
|  | HW_TEST_FAILURE | 15 | [8 empty] | Hardware test failure
|  | MANUFACTURER_ALRM | 16 | [8 empty] | Manfacturer alarm | Manufacturer alarm, see ManAlrmInfo field for more information.
Summary
7 |  | W |  |  | int16 |  | W_SF | W |  |  |  | Active Power | Total active power. | The active power being injected or absorbed in watts. The value is positive if power is being injected and negative if power is being absorbed.
8 |  | VA |  |  | int16 |  | VA_SF | VA |  |  |  | Apparent Power | Total apparent power. | The apparent power being injected or absorbed in volt-amps. The value is positive if power is being injected and negative if power is being absorbed.
9 |  | Var |  |  | int16 |  | Var_SF | Var |  |  |  | Reactive Power | Total reactive power. | The reactive power being injected or absorbed in volt-amps. The value is positive if power is being injected and negative if power is being absorbed.
10 |  | PF |  |  | int16 |  | PF_SF |  |  |  |  | Power Factor | Power factor. | The power factor as computed by xxx. [Should it be signed?]
11 |  | A |  |  | int16 |  | A_SF | A |  |  |  | Total AC Current | Total AC current. | The total AC current being injected or absorbed in amps. The value is positive if power is being injected and negative if power is being absorbed.
12 |  | LLV |  |  | int16 |  | V_SF | V |  |  |  | Voltage LL | Line to line AC voltage as an average of active phases.
13 |  | LNV |  |  | int16 |  | V_SF | V |  |  |  | Voltage LN | Line to neutral AC voltage as an average of active phases.
14 |  | Hz |  |  | int16 |  | Hz_SF | Hz |  |  |  | Frequency | AC frequency.
15 |  | TotWhInj |  |  | acc64 |  | TotWh_SF | Wh |  |  |  | Total Energy Injected | Total active energy injected (Quadrants 1 & 4).
19 |  | TotWhAbs |  |  | acc64 |  | TotWh_SF | Wh |  |  |  | Total Energy Absorbed | Total active energy absorbed (Quadrants 2 & 3).
23 |  | TotVarhInj |  |  | acc64 |  | TotVar_SF | Varh |  |  |  | Total Reactive Energy Inj | Total reactive energy injected (Quadrants 1 & 2).
27 |  | TotVarhAbs |  |  | acc64 |  | TotVar_SF | Varh |  |  |  | Total Reactive Energy Abs | Total reactive energy absorbed (Quadrants 3 & 4).
Temperatures
31 |  | TmpAmb |  |  | int16 |  | Tmp_SF | C |  |  |  | Ambient Temperature | Ambient temperature.
32 |  | TmpCab |  |  | int16 |  | Tmp_SF | C |  |  |  | Cabinet Temperature | Cabinet temperature.
33 |  | TmpSnk |  |  | int16 |  | Tmp_SF | C |  |  |  | Heat Sink Temperature | Heat sink temperature.
34 |  | TmpTrns |  |  | int16 |  | Tmp_SF | C |  |  |  | Transformer Temperature | Transformer temperature.
35 |  | TmpSw |  |  | int16 |  | Tmp_SF | C |  |  |  | IGBT/MOSFET Temperature | IGBT/MOSFET temperature.
36 |  | TmpOt |  |  | int16 |  | Tmp_SF | C |  |  |  | Other Temperature | Other temperature.
L1
37 |  | WL1 |  |  | int16 |  | W_SF | W |  |  |  | Watts L1 | Active power L1.
38 |  | VAL1 |  |  | int16 |  | VA_SF | VA |  |  |  | VA L1 | Apparent power L1.
39 |  | VarL1 |  |  | int16 |  | Var_SF | Var |  |  |  | Var L1 | Reactive power L1.
40 |  | PFL1 |  |  | int16 |  | PF_SF |  |  |  |  | PF L1 | Power factor phase L1.
41 |  | AL1 |  |  | int16 |  | A_SF | A |  |  |  | Amps L1 | Current phase L1.
42 |  | VL1L2 |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage L1-L2 | Phase voltage L1-L2.
43 |  | VL1 |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage L1-N | Phase voltage L1-N.
44 |  | TotWhInjL1 |  |  | acc64 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Inj L1 | Total active energy injected L1.
48 |  | TotWhAbsL1 |  |  | acc64 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Abs L1 | Total active energy absorbed L1.
52 |  | TotVarhInjL1 |  |  | acc64 |  | TotVarh_SF | Varh |  |  |  | Total Var-hours Inj L1 | Total reactive energy injected L1.
56 |  | TotVarhAbsL1 |  |  | acc64 |  | TotVarh_SF | Varh |  |  |  | Total Var-hours Abs L1 | Total reactive energy absorbed L1.
L2
60 |  | WL2 |  |  | int16 |  | W_SF | W |  |  |  | Watts L2 | Active power L2.
61 |  | VAL2 |  |  | int16 |  | VA_SF | VA |  |  |  | VA L2 | Apparent power L2.
62 |  | VarL2 |  |  | int16 |  | Var_SF | Var |  |  |  | Var L2 | Reactive power L2.
63 |  | PFL2 |  |  | int16 |  | PF_SF |  |  |  |  | PF L2 | Power factor L2.
64 |  | AL2 |  |  | int16 |  | A_SF | A |  |  |  | Amps L2 | Current L2.
65 |  | VL2L3 |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage L2-L3 | Phase voltage L2-L3.
66 |  | VL2 |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage L2-N | Phase voltage L2-N.
67 |  | TotWhInjL2 |  |  | acc64 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Inj L2 | Total active energy injected L2.
71 |  | TotWhAbsL2 |  |  | acc64 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Abs L2 | Total active energy absorbed L2.
75 |  | TotVarhInjL2 |  |  | acc64 |  | TotVarh_SF | Varh |  |  |  | Total Var-hours Inj L2 | Total reactive energy injected L2.
79 |  | TotVarhAbsL2 |  |  | acc64 |  | TotVarh_SF | Varh |  |  |  | Total Var-hours Abs L2 | Total reactive energy absorbed L2.
L3
83 |  | WL3 |  |  | int16 |  | W_SF | W |  |  |  | Watts L3 | Active power L3.
84 |  | VAL3 |  |  | int16 |  | VA_SF | VA |  |  |  | VA L3 | Apparent power L3.
85 |  | VarL3 |  |  | int16 |  | Var_SF | Var |  |  |  | Var L3 | Reactive power L3.
86 |  | PFL3 |  |  | int16 |  | PF_SF |  |  |  |  | PF L3 | Power factor L3.
87 |  | AL3 |  |  | int16 |  | A_SF | A |  |  |  | Amps L3 | Current L3.
88 |  | VL3L1 |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage L3-L1 | Phase voltage L3-L1.
89 |  | VL3N |  |  | int16 |  | V_SF | V |  |  |  | Phase Voltage L3-N | Phase voltage L3-N.
90 |  | TotWhInjL3 |  |  | acc64 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Inj L3 | Total active energy injected L3.
94 |  | TotWhAbsL3 |  |  | acc64 |  | TotWh_SF | Wh |  |  |  | Total Watt-hours Abs L3 | Total active energy absorbed L3.
98 |  | TotVarhInjL3 |  |  | acc64 |  | TotVarh_SF | Varh |  |  |  | Total Var-hours Inj L3 | Total reactive energy injected L3.
102 |  | TotVarhAbsL3 |  |  | acc64 |  | TotVarh_SF | Varh |  |  |  | Total Var-hours Abs L3 | Total reactive energy absorbed L3.
Active Power Throttling
106 |  | ThrotPct |  |  | int16 |  |  | Pct |  |  |  | Throttling in Pct | Throttling in Pct of maximum active power.
107 |  | ThrotSrc |  |  | bitfield32 | [6 empty] | Throttle Source Information | Active throttling source.
|  | MAX_W | 0
|  | FIXED_W | 1
|  | FIXED_VAR | 2
|  | FIXED_PF | 3
|  | VOLT_VAR | 4
|  | FREQ_WATT | 5
|  | DYN_REACT_CURR | 7
|  | LVRT | 8
|  | HVRT | 9
|  | WATT_VAR | 10
|  | VOLT_WATT | 11
|  | SCHEDULED | 12
|  | LFRT | 13
|  | HFRT | 14
|  | DERATED | 15
Scale Factors
109 |  | A_SF |  |  | sunssf | [5 empty] | S | Current Scale Factor | Current scale factor.
110 |  | V_SF |  |  | sunssf | [5 empty] | S | Voltage Scale Factor | Voltage scale factor.
111 |  | Hz_SF |  |  | sunssf | [5 empty] | S | Frequency Scale Factor | Frequency scale factor.
112 |  | W_SF |  |  | sunssf | [5 empty] | S | Active Power Scale Factor | Active power scale factor.
113 |  | PF_SF |  |  | sunssf | [5 empty] | S | Power Factor Scale Factor | Power factor scale factor.
114 |  | VA_SF |  |  | sunssf | [5 empty] | S | Apparent Power Scale Factor | Apparent power scale factor.
115 |  | Var_SF |  |  | sunssf | [5 empty] | S | Reactive Power Scale Factor | Reactive power scale factor.
116 |  | TotWh_SF |  |  | sunssf | [5 empty] | S | Active Energy Scale Factor | Active energy scale factor.
117 |  | TotVarh_SF |  |  | sunssf | [5 empty] | S | Reactive Energy Scale Factor | Reactive energy scale factor.
118 |  | Tmp_SF |  |  | sunssf | [5 empty] | S | Temperature Scale Factor | Temperature scale factor.
Manufacturer Alarm Information
119 |  | ManAlrmInfo |  |  | string | 32 | [5 empty] | Manufacturer Alarm Info | Manufacturer alarm information. Valid if MANUFACTURER_ALRM indication is active.

## 702
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description
|  | DERCapacity |  |  | group | [6 empty] | DER Capacity | DER capacity model.
0 |  | ID | 702 |  | uint16 |  |  |  |  | M | S | DER Capacity Model ID | DER capacity model id.
1 |  | L |  |  | uint16 |  |  |  |  | M | S | DER Capacity Model Length | DER capacity name model length.
Nameplate Ratings - Specifies capacity ratings
2 |  | WMaxRtg |  |  | uint16 |  | W_SF | W |  |  |  | Active Power Max Rating | Maximum active power rating at unity power factor in watts.
3 |  | WOvrExtRtg |  |  | uint16 |  | W_SF | W |  |  |  | Active Power (Over-Excited) Rating | Active power rating at specified over-excited power factor in watts.
4 |  | WOvrExtRtgPF |  |  | uint16 |  | PF_SF |  |  |  |  | Specified Over-Excited PF | Specified over-excited power factor.
5 |  | WUndExtRtg |  |  | uint16 |  | W_SF | W |  |  |  | Active Power (Under-Excited) Rating | Active power rating at specified under-excited power factor in watts.
6 |  | WUndExtRtgPF |  |  | uint16 |  | PF_SF |  |  |  |  | Specified Under-Excited PF | Specified under-excited power factor.
7 |  | VAMaxRtg |  |  | uint16 |  | VA_SF | VA |  |  |  | Apparent Power Max Rating | Maximum apparent power rating in voltamperes.
8 |  | VarMaxInjRtg |  |  | uint16 |  | Var_SF | Var |  |  |  | Reactive Power Injected Rating | Maximum injected reactive power rating in vars.
9 |  | VarMaxAbsRtg |  |  | uint16 |  | Var_SF | Var |  |  |  | Reactive Power Absorbed Rating | Maximum absorbed reactive power rating in vars.
10 |  | WChaRteMaxRtg |  |  | uint16 |  | W_SF | W |  |  |  | Charge Rate Max Rating | Maximum active power charge rate in watts.
11 |  | WDisChaRteMaxRtg |  |  | uint16 |  | W_SF | W |  |  |  | Discharge Rate Max Rating | Maximum active power discharge rate in watts.
12 |  | VAChaRteMaxRtg |  |  | uint16 |  | VA_SF | VA |  |  |  | Charge Rate Max VA Rating | Maximum apparent power charge rate in voltamperes.
13 |  | VADisChaRteMaxRtg |  |  | uint16 |  | VA_SF | VA |  |  |  | Discharge Rate Max VA Rating | Maximum apparent power discharge rate in voltamperes.
14 |  | VNomRtg |  |  | uint16 |  | V_SF | V |  |  |  | AC Voltage Nominal Rating | AC voltage nominal rating.
15 |  | VMaxRtg |  |  | uint16 |  | V_SF | V |  |  |  | AC Voltage Max Rating | AC voltage maximum rating.
16 |  | VMinRtg |  |  | uint16 |  | V_SF | V |  |  |  | AC Voltage Min Rating | AC voltage minimum rating.
17 |  | AMaxRtg |  |  | uint16 |  | A_SF | A |  |  |  | AC Current Max Rating | AC current maximum rating in amps.
18 |  | PFOvrExtRtg |  |  | uint16 |  | PF_SF |  |  |  |  | PF Over-Excited Rating | Power factor over-excited rating.
19 |  | PFUndExtRtg |  |  | uint16 |  | PF_SF |  |  |  |  | PF Under-Excited Rating | Power factor under-excited rating.
20 |  | ReactSusceptRtg |  |  | uint16 |  | S_SF | S |  |  |  | Reactive Susceptance | Reactive susceptance that remains connected to the Area EPS in the cease to energize and trip state.
21 |  | NorOpCatRtg |  |  | enum16 | [6 empty] | Normal Operating Category | Normal operating performace category as specified in IEEE 1547-2018.
|  | CAT_A | 1
|  | CAT_B | 2
22 |  | AbnOpCatRtg |  |  | enum16 | [6 empty] | Abnormal Operating Category | Abnormal operating performance category as specified in IEEE 1547-2018.
|  | CAT_1 | 1
|  | CAT_2 | 2
|  | CAT_3 | 3
23 |  | CtrlModes |  |  | bitfield32 | [6 empty] | Supported Control Modes | Supported control mode functions.
|  | MAX_W | 0
|  | FIXED_W | 1
|  | FIXED_VAR | 2
|  | FIXED_PF | 3
|  | VOLT_VAR | 4
|  | FREQ_WATT | 5
|  | DYN_REACT_CURR | 7
|  | LVRT | 8
|  | HVRT | 9
|  | WATT_VAR | 10
|  | VOLT_WATT | 11
|  | SCHEDULED | 12
|  | LFRT | 13
|  | HFRT | 14
25 |  | IntIslandCatRtg |  |  | bitfield16 |  |  |  | RW |  |  | Intentional Island Categories | Intentional island categories
Settings - Used to adjust nameplate ratings
26 |  | WMax |  |  | uint16 |  |  | W | RW |  |  | Active Power Max Setting | Maximum active power setting used to adjust maximum active power setting.
27 |  | WMaxOvrExt |  |  | uint16 |  | W_SF | W | RW |  |  | Active Power (Over-Excited) Setting | Active power setting at specified over-excited power factor in watts.
28 |  | WOvrExtPF |  |  | uint16 |  | PF_SF |  | RW |  |  | Specified Over-Excited PF | Specified over-excited power factor.
29 |  | WMaxUndExt |  |  | uint16 |  | W_SF | W | RW |  |  | Active Power (Under-Excited) Setting | Active power setting at specified under-excited power factor in watts.
30 |  | WUndExtPF |  |  | uint16 |  | PF_SF |  | RW |  |  | Specified Under-Excited PF | Specified under-excited power factor.
31 |  | VAMax |  |  | uint16 |  |  | VA | RW |  |  | Apparent Power Max Setting | Maximum apparent power setting used to adjust maximum apparant power rating.
32 |  | AMax |  |  | uint16 |  |  | A | RW |  |  | AC Current Max Setting | Maximum AC current setting used to adjust maximum ac current rating.
33 |  | Vnom |  |  | uint16 |  |  | V | RW |  |  | Nominal AC Voltage Setting | Nominal AC voltage setting.
34 |  | VRefOfs |  |  | uint16 |  |  | V | RW |  |  | Nominal AC Voltage Offset Setting | Nominal AC voltage offset setting.
35 |  | VMax |  |  | uint16 |  |  | V | RW |  |  | AC Voltage Max Setting | AC voltage maximum setting used to adjust AC voltage maximum rating.
36 |  | VMin |  |  | uint16 |  |  | V | RW |  |  | AC Voltage Min Setting | AC voltage minimum setting used to adjust AC voltage maximum rating.
37 |  | VarMaxInj |  |  | uint16 |  |  | Var | RW |  |  | Reactive Power Injected Setting | Maximum injected reactive power setting used to adjust maximum injected reactive power rating.
38 |  | VarMaxAbs |  |  | uint16 |  |  | Var | RW |  |  | Reactive Power Absorbed Setting | Maximum absorbed reactive power setting used to adjust maximum absorbed reactive power rating.
39 |  | WChaRteMax |  |  | uint16 |  |  | W | RW |  |  | Charge Rate Max Setting | Maximum active power charge rate setting used to adjust maximum active power charge rate rating.
40 |  | WDisChaRteMax |  |  | uint16 |  |  | W | RW |  |  | Discharge Rate Max Setting | Maximum active power discharge rate setting used to adjust maximum active power discharge rate rating.
41 |  | VAChaRteMax |  |  | uint16 |  |  | VA | RW |  |  | Charge Rate Max VA Setting | Maximum apparent power charge rate setting used to adjust maximum apparent power charge rate rating.
42 |  | VADisChaRteMax |  |  | uint16 |  |  | VA | RW |  |  | Discharge Rate Max VA Setting | Maximum apparent power discharge rate setting used to adjust maximum apparent power discharge rate rating.
43 |  | IntIslandCat |  |  | bitfield16 |  |  |  | RW |  |  | Intentional Island Categories | Intentional island categories
Scale Factors
44 |  | W_SF |  |  | sunssf | [5 empty] | S | Active Power Scale Factor | Active power scale factor.
45 |  | PF_SF |  |  | sunssf | [5 empty] | S | Power Factor Scale Factor | Power factor scale factor.
46 |  | VA_SF |  |  | sunssf | [5 empty] | S | Apparent Power Scale Factor | Apparent power scale factor.
47 |  | Var_SF |  |  | sunssf | [5 empty] | S | Reactive Power Scale Factor | Reactive power scale factor.
48 |  | V_SF |  |  | sunssf | [5 empty] | S | Voltage Scale Factor | Voltage scale factor.
49 |  | A_SF |  |  | sunssf | [5 empty] | S | Current Scale Factor | Current scale factor.
50 |  | S_SF |  |  | sunssf | [5 empty] | S | Susceptance Scale Factor | Susceptance scale factor.

## 703
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description
|  | DEREnterService |  |  | group | [6 empty] | Enter Service | Enter service.
0 |  | ID | 703 |  | uint16 |  |  |  |  | M | S | Enter Service ID | Enter service model id.
1 |  | L | 12 |  | uint16 |  |  |  | RW | M | S | Enter Service Length | Enter service model length.
2 |  | ES |  |  | enum16 |  |  |  | RW |  |  | Permit Enter Service | Permit enter service.
|  | DISABLED | 0
|  | ENABLED | 1
3 |  | ESVHi |  |  | uint16 |  | V_SF | Pct | RW |  |  | Enter Service Voltage High | Enter service voltage high threshold as percent of normal voltage.
4 |  | ESVLo |  |  | uint16 |  | V_SF | Pct | RW |  |  | Enter Service Voltage Low | Enter service voltage low threshold as percent of normal voltage.
5 |  | ESHzHi |  |  | uint32 |  | Hz_SF | Hz | RW |  |  | Enter Service Frequency High | Enter service frequency high threshold.
7 |  | ESHzLo |  |  | uint32 |  | Hz_SF | Hz | RW |  |  | Enter Service Frequency Low | Enter service frequency low threshold.
9 |  | ESDlyTms |  |  | uint16 |  |  | Secs | RW |  |  | Enter Service Delay Time | Enter service delay time in seconds.
10 |  | ESRndTms |  |  | uint16 |  |  | Secs | RW |  |  | Enter Service Random Delay | Enter service random delay in seconds.
11 |  | ESRmpTms |  |  | uint16 |  |  | Secs | RW |  |  | Enter Service Ramp Time | Enter service ramp time in seconds.
12 |  | V_SF |  |  | sunssf | [5 empty] | S | Voltage Scale Factor | Voltage scale factor.
13 |  | Hz_SF |  |  | sunssf | [5 empty] | S | Frequency Scale Factor | Frequency scale factor.

## 704
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description
|  | DERCtlAC |  |  | group | [6 empty] | DER AC Controls | DER AC controls model.
0 |  | ID | 704 |  | uint16 |  |  |  |  | M | S | Model ID | Model name model id.
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | Model name model length.
Set Power Factor (when injecting active power)
2 |  | PFWInjEna |  |  | enum16 |  |  |  | RW |  |  | Power Factor Enable (W Inj) Enable | Power factor enable when injecting active power.
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
3 |  | PFWInjEnaRvrt |  |  | enum16
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
4 |  | PFWInjRvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | PF Reversion Time (W Inj) | Power factor reversion timer when injecting active power.
6 |  | PFWInjRvrtRem |  |  | uint32 |  |  | Secs |  |  |  | PF Reversion Time Rem (W Inj) | Power factor reversion time remaining when injecting active power.
Set Power Factor (when absorbing active power)
8 |  | PFWAbsEna |  |  | enum16 |  |  |  | RW |  |  | Power Factor Enable (W Abs) Enable | Power factor enable when absorbing active power.
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
9 |  | PFWAbsEnaRvrt |  |  | enum16
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
10 |  | PFWAbsRvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | PF Reversion Time (W Abs) | Power factor reversion timer when absorbing active power.
12 |  | PFWAbsRvrtRem |  |  | uint32 |  |  | Secs |  |  |  | PF Reversion Time Rem (W Abs) | Power factor reversion time remaining when absorbing active power.
Limit Maximum Active Power Generation
14 |  | WMaxLimEna |  |  | enum16 |  |  |  | RW |  |  | Limit Max Active Power Enable | Limit maximum active power enable.
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
15 |  | WMaxLim |  |  | uint16 |  | WMaxLim_SF | Pct | RW |  |  | Limit Max Power Setpoint | Limit maximum active power value.
16 |  | WMaxLimRvrt |  |  | uint16 |  | WMaxLim_SF | Pct | RW |  |  | Reversion Limit Max Power | Reversion limit maximum active power value.
17 |  | WMaxLimEnaRvrt |  |  | enum16
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
18 |  | WMaxLimRvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | Limit Max Power Reversion Time | Limit maximum active power reversion time.
20 |  | WMaxLimRvrtRem |  |  | uint32 |  |  | Secs |  |  |  | Limit Max Power Rev Time Rem | Limit maximum active power reversion time remaining.
Set Active Power Level (may be negative for charging)
22 |  | WSetEna |  |  | enum16 |  |  |  | RW |  |  | Set Active Power Enable | Set active power enable.
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
23 |  | WSetMod |  |  | enum16 |  |  |  | RW |  |  | Set Active Power Mode | Set active power mode.
|  | W_MAX_PCT | 1 | [8 empty] | Active Power As Max Percent | Active power setting is percentage of maximum active power.
|  | WATTS | 2 | [8 empty] | Active Power As Watts | Active power setting is in watts.
24 |  | WSet |  |  | int32 |  | WSet_SF | W | RW |  |  | Active Power Setpoint (W) | Active power setting value in watts.
26 |  | WSetRvrt |  |  | int32 |  | WSet_SF | W | RW |  |  | Reversion Active Power (W) | Reversion active power setting value in watts.
28 |  | WSetPct |  |  | int32 |  | WSetPct_SF | Pct | RW |  |  | Active Power Setpoint (Pct) | Active power setting value as percent.
30 |  | WSetPctRvrt |  |  | int32 |  | WSetPct_SF | Pct | RW |  |  | Reversion Active Power (Pct) | Reversion active power setting value as percent.
32 |  | WSetEnaRvrt |  |  | enum16
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
33 |  | WSetRvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | Active Power Reversion Time | Set active power reversion time.
35 |  | WSetRvrtRem |  |  | uint32 |  |  | Secs |  |  |  | Active Power Rev Time Rem | Set active power reversion time remaining.
Set Reacitve Power Level
37 |  | VarSetEna |  |  | enum16 |  |  |  | RW |  |  | Set Reactive Power Enable | Set reactive power enable.
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
38 |  | VarSetMod |  |  | enum16 |  |  |  | RW |  |  | Set Reactive Power Mode | Set reactive power mode.
|  | W_MAX_PCT | 1 | [8 empty] | Reactive Power as Watt Max Pct | Reactive power setting is percent of maximum active power.
|  | VAR_MAX_PCT | 2 | [8 empty] | Reactive Power as Var Max Pct | Reactive power setting is percent of maximum reactive power.
|  | VAR_AVAIL_PCT | 3 | [8 empty] | Reactive Power as Var Avail Pct | Reactive power setting is percent of available reactive power.
|  | VARS | 4 | [8 empty] | Reactive Power as Vars | Reactive power is in vars.
39 |  | VarSetPri |  |  | enum16
|  | ACTIVE | 1 | [8 empty] | Active Power Priority | Active power priority.
|  | REACTIVE | 2 | [8 empty] | Reactive Power Priority | Reactive power priority.
|  | IEEE_1547 | 3 | [8 empty] | IEEE 1547 Power Priority | IEEE 1547-2018 power priority mode.
|  | PF | 4 | [8 empty] | PF Power Priority | Track PF setting derived from current active and reactive power settings.
|  | VENDOR | 5 | [8 empty] | Vendor Power Priority | Power priority is vendor specific mode.
40 |  | VarSet |  |  | int32 |  | VarSet_SF | Var | RW |  |  | Reactive Power Setpoint (Vars) | Reactive power setting value in vars.
42 |  | VarSetRvrt |  |  | int32 |  | VarSet_SF | Var | RW |  |  | Reversion Reactive Power (Vars) | Reversion reactive power setting value in vars.
44 |  | VarSetPct |  |  | int32 |  | VarSetPct_SF | Pct | RW |  |  | Reactive Power Setpoint (Pct) | Reactive power setting value as percent.
46 |  | VarSetPctRvrt |  |  | enum16 |  | VarSetPct_SF | Pct | RW |  |  | Reversion Reactive Power (Pct) | Reversion reactive power setting value as percent.
|  | DISABLED | 0 | [8 empty] | Disabled | Function is disabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is enabled.
47 |  | VarSetRvrtTms |  |  | uint32 |  |  | Secs | RW |  |  | Reactive Power Reversion Time | Set reactive power reversion time.
49 |  | VarSetRvrtRem |  |  | uint32 |  |  | Secs |  |  |  | Reactive Power Rev Time Rem | Set reactive power reversion time remaining.
Ramp Rate
51 |  | RGra |  |  | uint32 |  |  | %WMax/Sec | RW |  |  | Normal Ramp Rate | Ramp rate for increases in active power during normal generation.
|  | A_MAX | 1 | [8 empty] | Max Current Ramp | Ramp based on percent of max current per second.
|  | W_MAX | 2 | [8 empty] | Max Active Power Ramp | Ramp based on percent of max active power per second.
Scale Factors
53 |  | PF_SF |  |  | sunssf | [5 empty] | S | Power Factor Scale Factor | Power factor scale factor.
54 |  | WMaxLim_SF |  |  | sunssf | [5 empty] | S | Limit Max Power Scale Factor | Limit maximum power scale factor.
55 |  | WSet_SF |  |  | sunssf | [5 empty] | S | Active Power Scale Factor | Active power scale factor.
56 |  | WSetPct_SF |  |  | sunssf | [5 empty] | S | Active Power Pct Scale Factor | Active power pct scale factor.
57 |  | VarSet_SF |  |  | sunssf | [5 empty] | S | Reactive Power Scale Factor | Reactive power scale factor.
58 |  | VarSetPct_SF |  |  | sunssf | [5 empty] | S | Reactive Power Pct Scale Factor | Reactive power pct scale factor.
Power Factor Settings
|  | DERCtlAC.PFWInj |  |  | sync
| 0 | PF |  |  | uint16 |  | PF_SF |  | RW |  |  | Power Factor (W Inj) | Power factor setpoint when injecting active power.
| 1 | Ext |  |  | enum16 |  |  |  | RW |  |  | Power Factor Excitation (W Inj) | Power factor excitation setpoint when injecting active power.
|  | OVER_EXCITED | 0 | [8 empty] | Over-excited | Power factor over-excited excitation.
|  | UNDER_EXCITED | 1 | [8 empty] | Under-excited | Power factor under-excited excitation.
|  | DERCtlAC.PFWInjRvrt |  |  | sync
| 0 | PF |  |  | uint16 |  | PF_SF |  | RW |  |  | Reversion Power Factor (W Inj) | Reversion power factor setpoint when injecting active power.
| 1 | Ext |  |  | enum16 |  |  |  | RW |  |  | Reversion PF Excitation (W Inj) | Reversion power factor excitation setpoint when injecting active power.
|  | OVER_EXCITED | 0 | [8 empty] | Over-excited | Power factor over-excited excitation.
|  | UNDER_EXCITED | 1 | [8 empty] | Under-excited | Power factor under-excited excitation.
|  | DERCtlAC.PFWAbs |  |  | sync
| 0 | PF |  |  | uint16 |  | PF_SF |  | RW |  |  | Power Factor (W Abs) | Power factor setpoint when absorbing active power.
| 1 | Ext |  |  | enum16 |  |  |  | RW |  |  | Power Factor Excitation (W Abs) | Power factor excitation setpoint when absorbing active power.
|  | OVER_EXCITED | 0 | [8 empty] | Over-excited | Power factor over-excited excitation.
|  | UNDER_EXCITED | 1 | [8 empty] | Under-excited | Power factor under-excited excitation.
|  | DERCtlAC.PFWAbsRvrt |  |  | sync
| 0 | PF |  |  | uint16 |  | PF_SF |  | RW |  |  | Reversion Power Factor (W Abs) | Reversion power factor setpoint when absorbing active power.
| 1 | Ext |  |  | enum16 |  |  |  | RW |  |  | Reversion PF Excitation (W Abs) | Reversion power factor excitation setpoint when absorbing active power.
|  | OVER_EXCITED | 0 | [8 empty] | Over-excited | Power factor over-excited excitation.
|  | UNDER_EXCITED | 1 | [8 empty] | Under-excited | Power factor under-excited excitation.

## 705
Address Offset | Group Offset | Name | Value | Count | Type | Size | Scale Factor | Units | RW Access (RW) | Mandatory (M) | Static (S) | Label | Description | Detailed Description
|  | DERVoltVar |  |  | group | [6 empty] | DER Volt-Var | DER Volt-Var model.
0 |  | ID | 705 |  | uint16 |  |  |  |  | M | S | Model ID | DER Volt-Var model id.
1 |  | L |  |  | uint16 |  |  |  |  | M | S | Model Length | DER Volt-Var model length.
2 |  | Ena |  |  | enum16 |  |  |  | RW | M |  | Module Enable | Is Volt-Var control active.
|  | DISABLED | 0 | [8 empty] | Disabled | Function is enabled.
|  | ENABLED | 1 | [8 empty] | Enabled | Function is disabled.
3 |  | CrvSt |  |  | enum16 |  |  |  |  | M |  | Active Curve State | Current active curve state.
|  | INACTIVE | 0 | [8 empty] | No active curve | No curve is currenly active.
|  | ACTIVE | 1 | [8 empty] | Active curve enabled | Active curve in effect.
4 |  | AdptCrvReq |  |  | uint16 |  |  |  | RW | M |  | Set active curve request | Set active curve. 0 = No active curve
5 |  | AdptCrvRslt |  |  | enum16 |  |  |  |  | M |  | Set active curve result | Result of last set active curve operation.
|  | IN_PROGRESS | 0 | [8 empty] | Update In Progress | Curve update in progress.
|  | COMPLETED | 1 | [8 empty] | Update Complete | Curve update completed successfully.
|  | FAILED | 2 | [8 empty] | Update Failed | Curve update failed.
6 |  | NPt |  |  | uint16 |  |  |  |  | M | S | Number of Points | Number of curve points supported.
7 |  | NCrv |  |  | uint16 |  |  |  |  | M | S | Stored Curve Count | Number of stored curves supported.
8 |  | RvrtTms |  |  | uint32 |  |  |  | RW |  |  | Reversion timeout | Reversion time in seconds. 0 = No reversion time
10 |  | RvrtRem |  |  | uint32 | [6 empty] | Reversion time left | Reversion time remaining in seconds
12 |  | RvrtCrv |  |  | uint16 |  |  |  | RW |  |  | Reversion curve | Default curve after reversion timeout.
13 |  | V_SF |  |  | sunssf |  |  |  |  | M | S | Voltage Scale Factor | Scale factor for curve voltage points.
14 |  | DeptRef_SF |  |  | sunssf |  |  |  |  | M | S | Var Scale Factor | Scale factor for curve var points.
Stored Curve Sets - Number of curve sets contained in NCrv
|  | DERVoltVar.Crv |  | NCrv | group | [6 empty] | Stored Curves | Stored curve sets.
| 0 | ActPt |  |  | uint16 |  |  |  | RW | M |  | Active Points | Number of active points.
| 1 | DeptRef |  |  | enum16 |  |  |  | RW | M |  | Dependent Reference | Curve dependent reference.
|  | W_MAX_PCT | 1 | [8 empty] | Percent Max Watts
|  | VAR_MAX_PCT | 2 | [8 empty] | Percent Max Vars
|  | VAR_AVAL_PCT | 3 | [8 empty] | Percent Available Vars
| 2 | Pri |  |  | enum16
|  | ACTIVE | 1 | [8 empty] | Active Power Priority | Active power priority.
|  | REACTIVE | 2 | [8 empty] | Reactive Power Priority | Reactive power priority.
|  | IEEE_1547 | 3 | [8 empty] | IEEE 1547 Power Priority | IEEE 1547-2018 power priority mode.
|  | PF | 4 | [8 empty] | PF Power Priority | Track PF setting derived from current active and reactive power settings.
|  | VENDOR | 5 | [8 empty] | Vendor Power Priority | Power priority is vendor specific mode.
| 3 | VRef |  |  | uint16 |  |  |  | RW |  |  | Vref adjustment | Vref adjustment as percentage.
| 4 | VRefAuto |  |  | bitfield16 |  |  |  | RW |  |  | Autonomous Vref Enable | Enable automonous vref
|  | ENABLED | 0 | [8 empty] | Enabled Flag | Enabled flag (Disabled = 0, Enabled = 1).
| 5 | VRefTms |  |  | uint16 |  |  |  | RW |  |  | Auto Vref Time Constant | Autonomous vref time constant.
| 6 | RspTms |  |  | uint16 |  |  |  | RW |  |  | Open Loop Response Time | Open loop response time.
| 7 | ReadOnly |  |  | enum16 |  |  |  | RW |  |  | Curve Access | Curve read-write access.
|  | RW | 0 | [8 empty] | Read-Write Access | Curve has read-write access.
|  | R | 1 | [8 empty] | Read-Only Access | Curve has read-only access.
Stored Curve Sets - Curve points for each stored curve - Number of curve points contained in NPt
|  | DERVoltVar.Crv.Pt |  | NPt | group | [6 empty] | Stored Curve Points | Stored curve points.
| 0 | V |  |  | uint16 |  |  | VRefPct | RW | M |  | Voltage Point | Curve voltage point as percentage.
| 1 | Var |  |  | int16 |  | DeptRef_SF | VarPct | RW | M |  | Reactive Power Point | Curve reactive power point as set in DeptRef point.